## Sheet1
TasTAFE 75 Campbell St Hobart
Basement and Ground Floor Automotive Workshops
TCM Job 47813
| WO WOS 03012 | 2024-11-11
Investigation of Ventilation in the Workshops
| System | Serves | Information on the Operation | Questions
Basement
A | Basement South | Aurora 1 & 2 | Inline Fan to 1200 x 900 louvre controlled by T'Stat | How is this system to be operated most effective
| Substation Exhaust |  | Duct to two @ 400 x 200 grilles blanked inside Aurora 2 | would be a separate system for AB - 19 & 20
Make up air from Plant area via Aurora 1
Readings Taken 30/10/24
|  | Fan Airflow readings | Duct Pitot 9.1 m/sec Duct 0.1824 m2 Total Air 1650 lit/sec | 21.6 Air Changes per hour
Substation only
|  | Plant AB - 19 | No Ventilation to Plant only Ventilated Roller door
|  | Office AB - 20 | Blanked duct from Aurora 2 to a damper
No Ventilation to this area now an equipment store
B | Engine Workshop | Workshop AB - 02 | These 3 Spaces now 1 area | Inadequate Make up air
| Exhaust | Hydraulic Worksh AB - 17 | Workshop Ex System Duct 450 x 700 Axial Fan 500 dia | The space would be very cold in Winter if the system ran.
|  | Store AB - 18 | 7 Grilles 400 x 200 | Read the two system airflows with Roller open/shut
The Fan is manually controlled as required
Relief air is small classroom supply and damper below SA
|  | Fan GE-7 | Readings Taken 30/10/24 | Slight drop with Relief shut to 87%
|  | Fan Airflow readings | Duct Pitot 4.7 m/sec Duct 0.315 m2 Total Air 1480 lit/sec | 5.07 Air Changes per hour
C | Battery charging | AB - 27 | Dedicated Exhaust system | Check air 300 x 200 duct
Readings Taken 30/10/24
|  | Fan Airflow readings | Low grille 32 lit/sec High grille 89 lit/sec | 20.1 Air Changes per hour
D | Classroom & Store | AB - 03, 04 & 06. | Filtered Supply air to 3 Cassette units | Read the Supply air flow big load on the cassette units
| Fresh air |  | Readings Taken 30/10/24
|  | Fan Airflow readings | Duct Pitot 1.3 m/sec Duct 0.12 m2 Total Air 150 lit/sec
E | Engine Exhaust | AB - 02 | Engine Muffler Exhaust from 3 Reels to fan in Dyno Room | Duct 300 x 400 to Nederman Fan
Readings Taken 30/10/24
|  | Fan Airflow readings | Duct Pitot 2.125 m/sec Duct 0.105 m2 Total Air 223 lit/sec
G | Cars & Dyno | AB - 01 | South Exhaust system 500 x 700 duct | Inadequate Make up air
| Workshop South |  | 7 grilles sizes vary | The space would be very cold in Winter if the system ran.
|  |  | No Makeup pathway Manual control switch | Read the two system airflows with Roller open/shut
|  | Fan EF 05 | Readings Taken 30/10/24
|  | Fan Airflow readings | Duct Pitot 5.7 m/sec Duct 0.35 m2 Total Air 2000 lit/sec | 10.03 Air Changes per hour ( With GE 06)
H | Cars & Dyno | AB - 01 | North Exhaust system 500 x 450 duct discharge to carpark | As for South System
| Workshop North |  | 2 grilles 500 x 200
Duct has been blanked two grilles not exhausting
No Makeup pathway Manual control switch
|  | Fan EF 06 | Readings Taken 30/10/24
|  | Fan Airflow readings | Grille 1 520 lit/sec Grille 2 350 lit/sec Total Air 870 lit/sec | 10.03 Air Changes per hour ( With GE 05)
I | Engine Exhaust | AB - 01 | Engine Muffler Exhaust from 2 Reels | Duct 300 x 400 to Nederman Fan
|  | Fan EF Genesis | Readings Taken 30/10/24
|  | Fan Airflow readings | Duct Pitot 180 l.t/se + first flex 200 lit/sec Total 380 lit/sec
J | Engine Exhaust | AB - 01 | Central system 100 dia PVC silencer to Nederman fan | 100 to 80 dia system
4 muffler outlets and a capped outlet
Readings Taken 30/10/24
|  | Outlet Airflow readings | Hose 1- 9.0 m/sec, Hose 2- 6.5 m/sec, Hose 3 -13 m/sec
Plus an additional fixed 50dia pipe
K | Archives Space | AB - 13 | One vent at the Eastern end to the carpark 600 x 500
L | Welding Space | AB - 16 annex | Fixed vent with a ventilation problem | Relocate system from AG - 01 for welding
Wall fan for general clearence
M | Fuel Store | AB - 15 | Flammable liquid store in/out vents capped | Dedicated exhaust
N | Fuel Store | AB - 15 | Exhaust fan into carpark area not ex proof. | Review system
Readings Taken 30/10/24
|  | Fan Airflow readings | Grille 1 112 lit/sec | 7.2 Air Changes per hour
Ground
O | Motorbody W/S | AG - 40, 41 & 42, | Exhaust system 500 x 450 duct discharge to carpark | Read the two system airflows with Roller open/shut
|  | All now combined | 5 grilles 500 x 200 | Battery Charging area needs attention.
No Makeup pathway Manual control switch
Readings Taken 30/10/24
|  | Fan Airflow readings | Duct Pitot 6.61 m/sec Duct 0.2 m2 Total 1320 lit/sec | 18.3 Air Changes per hour
P | Engine Exhaust | AG - 40 | Engine Muffler Exhaust from 3 Reels | Duct 500 x 400 to Nederman Fan which discharges into
|  |  | Readings Taken 30/10/24 | the Bathurst St Carpark Exhaust System
|  | Fan Airflow readings | Duct Pitot 1 -2.44 m/sec Duct 0.09 m2 220 lit/sec
Duct Pitot 2 -2.28 m/sec Duct 0.045 m2 103 lit/sec
Q | Motor Batteries | AG - 40 | Flammable liquid store in/out vents open to the space | Dedicated exhaust
R | Small Engines | AG - 01 & 04 | Workshop walls gone and the space has many systems | Inadequate Make up air
|  |  | Exhaust system 700 x 450 duct discharge to carpark | The space would be very cold in Winter if the system ran.
|  |  | 6 grilles 400 x 250 and 2 grilles in AG - 03 | Read the two system airflows with Roller open/shut
No Makeup pathway Manual control switch
|  | Fan Airflow readings | Duct Pitot 1 -4.77 m/sec Duct 0.27 m2 1290 lit/sec | AG-01 6.63 Air Changes per hour
|  |  | Additional grilles Rm AG-03 665 lit/sec | AG-03 15 Air Changes per hour
Re balance to an even up to 8.04 Air Changes per hour
S | Engine Exhaust | AG - 01 | Engine Muffler Exhaust from 3 Reels | Duct 250 x 400 to Nederman Fan
|  | Fan Airflow readings | Duct Pitot -1.05 m/sec Duct 0.10 m2 Total 105 lit/sec
T | Engine Exhaust | AG - 01 | Engine Muffler Exhaust from 4 Reels on the floor | Duct 250 x 250 to Nederman Fan
U | Welding Bay Ex | AG - 04 | Welding Exhaust to 2 Nederman Arms | Duct 400 x 300 to Nederman fan
|  |  | Both outlets around 4.5 to 5 m/sec at the cone. | Consider relocating System to the Welding area AB - 16
This has a problem with welding gases.
V | Supply Air? | AG - 01 | Further investigation but connects to an insulated riser | Inadequate Make up air
|  |  | 4 Grilles 600 x 500 All Blanked off | Read the two system airflows with Roller open/shut
W | Workshop | AG - 03 | Exhaust from AG - 3 system | Makeup from AG - 01
| Fuel Injection |  | Local systems serving 2 Fuel Injection devices one open | Duct 450 x 200
X | Supply Duct | AG-04 | Not operation Comment blew out heaps of cold air | Could be some make up for the area with Filter added
Y | Exhust | AG-04 | Open duct not labeled 180 lit/sec | Additional to general Exhaust redundant AG-04